Contents

1 Overview	3

2 Preparations	3

2.1 Prerequisites	3

2.2 Deployment Process	3

3 Configuring Solarwinds Server & Application Monitor	4

Monitoring XFUSION Servers by Using Solarwinds Server & Application Monitor

Keywords: monitoring, SNMP, trap

Abstract: This document describes how to use Solarwinds Server & Application Monitor to monitor XFUSION servers.

Acronyms and Abbreviations: The following table lists acronyms and abbreviations used in this document.

| Acronym and Abbreviation | Full Spelling |
| --- | --- |

Overview

This document describes how to use Solarwinds Server & Application Monitor to monitor XFUSION servers through SNMP.

Preparations

Prerequisites

Test network diagram

IP address configuration:

Symantec Management Console IP address: 192.168.2.112    255.255.0.0

E9000 iBMC IP address: 192.168.12.10    255.255.0.0

E9000 HMM IP address: 192.168.10.1    255.255.0.0

Deployment Process

The steps are as follows:

Install and deploy Solarwinds Server & Application Monitor.

Set the network of Solarwinds Server & Application Monitor.

----End

Installing and Deploying Solarwinds Server & Application Monitor

Deploy Solarwinds Server & Application Monitor on the Windows Server 2012 OS.

You can download the software of the trial version from the official website. It is recommended that you download the offline package that included all the dependent software.

Official website: http://www.solarwinds.com/server-application-monitor

In normal cases, you can complete the installation process by clicking Next in sequence. In a test, the dependent .net 4.6.2 cannot be installed on the OS. To solve the problem, you need to update the OS patch.

Configuring Solarwinds Server & Application Monitor

After the installation is complete, use the software to access the WebUI of the control end, as shown in the following figure.

Choose Settings > Network Sonar Discovery, as shown in the following figure.

Click Start to perform network discovery configuration and import devices to be monitored in batches.

Set the community name on the SNMP tab.

On the MONITORING SETTINGS tab, select SNMP and Automatically monitor based on my defined monitoring settings.

Click Next in sequence to complete the configuration.

The monitoring automatically starts if SNMP is enabled on the server.

After the network discovery function is enabled, devices are monitored on the home page.

In addition, you can choose Settings > All Settings > Add Node to add a device to be monitored.

The monitoring results are as follows.

After the trap service of the server is enabled (the trap service is enabled by default), you can choose ALERTS & ACTIVITY > Traps to view the reported trap messages. (You can also view the trap messages on a node that is not added.)

Summary: Operations on Solarwinds are generally simple. However, MIB import is not supported. In current tests, it is found that the MIB library delivered with Solarwinds does not completely adapt to XFUSION servers, and fields in some SNMP trap messages cannot be resolved. The CPU and memory information of the iBMC can be monitored, but that of the HMM cannot be monitored. Currently, it is known that MIB library data files need to be created with the technical support of the software vendor and be imported to the software to implement MIB-related updates, and the software does not provide import interfaces that are directly developed. The technical support of the software, however, is only for customers who purchase the software.